## Slide 1
Introduction to the latest (draft) Data Centre FAQ and BAT
The FAQ started in 2016 as a repository of the developing regulatory and permitting approach to EA officers, NPS, legacy & new DC operators
It clarified and explained the issues rather than simply defining outcomes
It communicated best and common practice addressing new topics as they arose.
Early key BAT and modelling approach highest priorities
The FAQ has continued to develop in this way and regrettably is over 40 pages long but has not been issued/released recently.
It was anticipated to separate/edit down to a simple EA permitting/BAT and an Industry Code of Practice – which is unlikely to materialise soon
So the big caveat is that the FAQ has significant content but DRAFT; there is only so much that the lone author can take ownership: options, ‘TBC’s’ and ‘reviews/authorisation (E&B)’.
Edits and additions in red
Howard Tee
15/11/22

## Slide 2: Key Updates & Additions
Use of temporary plant – large scale needs added AQ risk assessment
Definition of Commissioning for (in advance) permitting
Expanding sites >50MWth permitted as new MCP initially – BAT expectations
Maintenance regime for optimum emissions – anymore suggestions?
Implications if Main power source not UKPN (landfills, EfW, solar panels) for contracting back on to Grid in an outage, reliability & probability of outages impacting AQ model
Clarity around 2g-Luft & EPA tier2 emissions optimised: tolerances
Propose consideration that BAT for commissioning new engines is a sample port confirming BAT emissions (2g/EPA Tier2)

## Slide 3: Key Updates & Additions
Using SCR to achieve 2g-Luft & EPA tier2 emissions optimised “Equivalence” (Full and Lite SCR defined)
Waste EWC codes listed and expected for Annual Reporting (Pollution Inventory)
AQ modelling advice & outcomes – inc completing the goals of the AQMP template
Good practice issues (but not strictly DAAs) coming up in inspections that might affect sites?
General agreement retro-fitting sample ports and doing ELV compliance not appropriate for standby overall.
HVO
SCR as BAT (Separate SCR BAT document in draft)
(Other stuff hidden in the now 42 page document!!!)

## Slide 4: Moving to SCR as BAT
Sector is expanding rapidly with significant balance change from ‘legacy’ to new build since 2017
New builds are getting bigger (MWth) with still larger engines
Expansion options for mega-scale (hyperscale) including buying up adjacent land after permitting
Increased awareness for receptors high peak NO & NO2
Increased operator awareness for workplace potential exposure during outages peak NO2
Sites fitting SCR abatement under planning in GLA for long term environmental costs (Air Quality Focus Areas AQFAs, Air Quality Neutral)
Under a Corporate precautionary & Green objectives basis for some operators
Clusters and associated concerns are increasing (sites permitted/assessed separately till now) for wider outages
Possible Options to increase pool of available new engines (marginally ‘non-emission optimised’) to allow more flexibility tolerances on 2g/EPA Tier2 BAT with SCR to achieve equivalence i.e. buying ‘do better SCR than the minimum’ as a package?
Future options to see the ‘standby diesel’ sector as an elective emergency resource

## Slide 5: Moving to SCR as BAT
The following points are noted for information:
  SCR is commonly regarded and taken to be the BAT secondary abatement option for diesel engines for NOx (without further justification in the FAQ not least because…)
  The MCP legal requirement ELV for diesel engines, new and existing plant >5MWth on gas-oil is 190mg/m3 at 15% O2 * (250mg/m3 for existing plant <5MWth)
  The exclusion from the above ELV is under Article6(8) – “Member states may exempt new MCP which to not operate >500hours per year”
  Engine BAT already assumes ‘BAT for Stacks’ and ‘BAT of having an AQMP’
Upshot: The EA is wishing to move to SCR as BAT under the review cycle of BAT for IED 1.1A(1)a large aggregated standby but under detailed, applicable criteria as follows.
*this ELV itself could be even tighter in AQMAs under MCP Article6(9)

## Slide 6: Criteria
  Emissions optimised 2g-TA Luft or US EPA tier 2 or equivalent – the current default BAT
  Outage ambient NOx peak limited & minimised due to scale or location/proximity of standby; or technically where the Peak NOx over short timescales (first 10mins to few hours) to sensitive receptors could hence not reasonably be managed via the AQMP:
    In any event (new or existing plant expanding aggregated}, plant fitted with SCR (full or lite etc) to all or most engines and abated to at least a level whereby no current or likely future sensitive receptor under outage for the whole or part site realistic loads peak NO or NO2 (NOx) exceeds a defined safe concentration limit – what is the safe limit TBC*?
      Target 99.7%ile 1 hour average off-site (cell max, any potential receptor) NO2 <600ug/m3 or better
      Absolute theoretical peak 100%ile on/off site AEGL1 (nearly =HSE Workplace exposure) NO2 940ug/m3 (being common concentration - 10min to 8hour value) {site specific justification of the averaging period based on ability to proactively engage AQMP with receptors – precautionary default 10mins, but consider 1hour}
      * Based on DEFRA Air Quality Index (see BreatheLondon) with an absolute peak:
      1304251155_Update_on_Implementation_of_the_DAQI_April_2013_Final.pdf (defra.gov.uk)

## Slide 7: Criteria
  Local Authority or regionally designated AQF, AQMPs, planning requirement and possibly designated clusters (notably Slough Trading Estate) – heightened BAT SCR-full+:
    Emissions optimised (2g/US EPA tier2) engines fitted with fast-response (<=10mins) full-SCR abatement achieving better than 90% reduction (ideally to at least an indicative 95mg/m3 at 15% O2)
  ADVISORY BAT “SCR-ready” configurations are included to allow retrospective fitting of SCR abatement if necessary
  SCR-Lite = 2g/US EPA tier2 ‘equivalence’ (750mg/m3 at 15% O2)
  SCR–full = MCP ELV compliance (190mg/m3 at 15% O2)
  SCR–full+ = 2g/ US EPA tier2 + with fast-response maximal SCR (<95mg/m3 at 15% O2) [risks NH3 slip issues?]
  Of currently 22 HNL permitted aggregated standby I reckon 4 would probably need some SCR, 15 maybes (so more detailed AQ remodelling at least), 7 unlikely

## Slide 8: Notes
  This is about de-linking likelihood of a prolonged outage to one of ‘in the event of any reasonable outage’ (or in some cases maintenance/tests too) operations, where, when and for how long could short peak NO2 (and NO) occur. This is looking at the process contribution PC/PEC and ultimately this may be equivalent to a site total mass emission rate (MWth density) - TBC
  It is generally recognised and currently permitted that achieving ST ambient AQ standard of <200ug/m3 at any location off-site for around 1 hour (let alone in a prolonged outage <18hours) for even some of the smallest aggregated sites (MCP scale) could be unachievable and disproportionate for reliably connected, emergency standby in urban settings. But ultimately this is the idealised target DAQI level for no pollution.
  EA specified generator modelling guidance: “You need to include the maximum hourly (100th percentile) NO2 PEC. This is to understand the potential health effects and the amount of risk to members of the public. There is no absolute hourly limit environmental standard for the acute exposure to NO2, but there can be effects on health over a certain threshold”.

## Slide 9: Review cycle of BAT (4-8 years) for IED 1.1A(1)a >50MWth for Aggregated Standby
2025
  Criteria defining when SCR as BAT applies (i.e. over emissions optimised plant) – new plant
  Agree SCR BAT for new plant and if needed CBA criteria for existing plant
  Technical aspects and operational BAT of SCR on diesel standby
  Opportunity for review of the FAQ of sector critical aspects of BAT (pick out anything for discussion, clarity or expansion generally – industry code of practice ICOP?)
  Scope for future proofing BAT beyond 2030
  Start reviewing existing stock of permits under a BAT review
2026
  Completed review of 1.1A(1)a aggregated standby (includes some non-data centres)
2030
  End of Four year period to implement BAT across the sector

## Slide 10: SCR as BAT for New:- the advantages Or put another why not start planning on fitting SCR just now?
Permitting on AQ should be easier for new plant?
Precautionary principle for future expansion and clusters
Clear benefit on short term peaks and overall AQ LT impacts
AQ environment is improving so unabated diesel standby will become a larger, more obvious source after 2030 (when current investments may still have 20+years)
Secondary benefits TBC could the sector agree an approach to allow UK identified emergency/resilience criteria – i.e. sites with SCR might be allowed to do demand-side response or limited export (but avoiding/incorporating a limited specified generator component)?