## Sheet1
Calculating fuel-oil consumption in a calander year for emergency generators in data centre applicaions
Note that as a low-emitter, estimation is allowable but must be as accurate as is possible, on a consistant basis from year-to-year and must withstand an audit | [11 empty] | 250 | Litres per MW/hour
[12 empty] | 50 | Litres per MW/hour at <20% load
Alternatively, if you record fuel combusted in a given year and can support the data from documented deliveries then enter actual Litres
combusted (NOT delivered) in B37, overwriting the calculation | [11 empty] | 50% | Load for testing
TRUE
Maintenance & testing of generator system | [11 empty] | 150 | Liters/hour/MW for genset testing | 0 | Litres
|  |  | Notes | [8 empty] | 150 | Liters/hour/MW for M&E Maintenance | 0 | Liters
Data Centre actual load | 10 | MW | Take the annualised kWh for the utility consumption from the PUE calculation, | [8 empty] | 150 | Liters/hour/MW for in anger operation | 360000 | Liters
e.g. Facility main transformer output
Generator installed capacity | 20 | MW | Include all generators, including redundant machines.
They will be listed as kVA or MVA and these should be converted to MW, e.g. x0.8 to convert MVA to MW or x(0.8/1000) to convert kVA to MW
Load used for testing | 10 | MW | This will depend upon your maintenance regime and should be only one of three options:
| 50% |  |  | 1) Data Centre actual load from B9 |  |  | 2) Size of the load bank, either fixed or rental |  |  |  | 3) No load, functional start testing only, enter zero
Maintenance Strategy | 0 | hours from Table 1
Table 1
Sub-total | 0 | Litres | Description of typical maintenance routine |  |  |  |  | Enter into B15
|  |  | A | 30 minutes per quarter, plus cool-down |  |  |  | 4 | Hours/annum | Cool-down is assumed as 15 minutes at zero-load
|  |  | B | 15 minutes per month, plus cool-down |  |  |  | 3 | Hours/annum | Cool-down is assumed as 15 minutes at zero-load
|  |  | C | 30 minutes per month, plus cool-down |  |  |  | 6 | Hours/annum | Cool-down is assumed as 15 minutes at zero-load
|  |  | D | 60 minutes per month, plus dool-down |  |  |  | 12 | Hours/annum | Cool-down is assumed as 15 minutes at zero-load
|  |  | E | Bespoke monthly maintenance regime |  |  |  | Actual | Hours/annum | Enter actual hours in K22 if A-D are unrepresentative
Maintenance of M&E using generators
Assumed load | 10 | MW | Unless an audit can prove otherwise the calculation assumes the actual data centre load from B9. Overwrite cell if justified and auditable
| 50% |  | e.g. in a concurrently maintainable system where annual maintenance requires a UPS shut-down for circa 4 hours
Hours in maintenance mode | 0 | hours | Note that a dual-bus power system may result in no generator operation for M&E maintenance
Sub-total | 0 | Litres
Generators starting in anger
Number of utility failures | 1 | N generator starts from BMS record from the PRIOR YEAR
Time spent on genset | 240 | hours from BMS record from the PRIOR YEAR
Sub-total | 360000 | Litres
Density From DUKES
Total Litres Estimated | 360000 | Litres |  |  | 1172 | litres/tonne
From National inventory data
Total Tonnes | 307.1672 |  |  |  | 43 | NCV (GJ/t)
[5 empty] | 74.1 | EF (TJ/t)
| 978.727 | Tonnes of CO2 |  |  | 1 | OxF